## RFI Response - Example
Simple Construction RFI Form Template - Example
RFI Name | Structural Beam Conflict with HVAC Duct |  | RFI ID | 2024-037
Requesting Party | ABC General Contractors |  | Responding Party | XYZ Mechanical Services
RFI Response Submission Deadline | XX/XX/XXXX |  | Date Of RFI Response | XX/XX/XXXX
Organization Name | XYZ Mechanical Services |  | Contact Name | Brian Gorman
Address | 789 Industrial Road, Suite 400 |  | Contact Title | Senior Project Engineer
| Los Angeles, CA 90012 |  | Phone | (555) 789-1234
Website |  |  | Email
Request Description
The current mechanical drawing (Sheet M202) shows a 36” x 18” HVAC duct running along the east corridor on Level 2. The structural drawing (Sheet S103) places a W18x40 steel beam in the same space, creating a conflict. The duct cannot pass through the beam location as designed. The general contractor has requested a resolution to this conflict before installation begins to prevent schedule delays.
Response
XYZ Mechanical Services has reviewed the conflict and proposes the following resolution options: Option 1: Duct Size Modification (Preferred Solution) Reduce the duct height from 18” to 14” to maintain airflow requirements while clearing the beam. Increase the duct width to 40” to compensate for the reduced height and maintain airflow volume. Verify updated dimensions with the structural and MEP engineers before implementation. Option 2: Duct Rerouting (Alternative Solution) Shift the duct 24” west to avoid the beam entirely. Rerouting will require a minor adjustment to sprinkler and electrical conduit layouts. This solution may affect ceiling height in adjacent rooms, requiring coordination with the architect. Estimated Impact on Cost & Schedule Option 1: No significant cost impact; minor fabrication changes. No additional time required. Option 2: Potential increase of $3,500 due to added duct material and labor. Requires two additional workdays. Next Steps & Approvals We recommend proceeding with Option 1, pending approval from the project structural engineer. Please confirm the selected solution by March 18, 2024, to prevent delays in mechanical system installation.
Response Prepared By |  | Brian Gorman, Senior Project Engineer
Attachments? |  | Yes - Marked-up drawings included | Number of Pages |  | 3
CLICK HERE TO CREATE IN SMARTSHEET

## RFI Response - Blank
Simple Construction RFI Form Template
RFI Name | RFI ID
Requesting Party | Responding Party
RFI Response Submission Deadline | Date Of RFI Response
Organization Name | Contact Name
Address | Contact Title
Phone
Website | Email
Request Description
Response
Response Prepared By
Attachments? | Number of Pages

## - Disclaimer -
Any articles, templates, or information provided by Smartsheet on the website are for reference only. While we strive to keep the information up to date and correct, we make no representations or warranties of any kind, express or implied, about the completeness, accuracy, reliability, suitability, or availability with respect to the website or the information, articles, templates, or related graphics contained on the website. Any reliance you place on such information is therefore strictly at your own risk.